Ignition Temperature vs. Temperature Markings

In general, the NEC stipulates that an operating temperature or temperature range marking appears on equipment approved for Division 1 Hazardous Locations. For motors, U.L. further clarifies that this marking is to indicate the maximum temperature for all conditions including overload, locked rotor and single-phasing.

Per the NEC, the temperature range marking is in the form of an Identification Number shown in the below. U.L. calls this a Code Number.

| T-Codes and Associated Temperature |
| --- |
| Identification Numbers |  |  |  |  |  | Maximum Temperature |
| T1 |  |  |  |  |  | 450°C | 842°C |
| T2 |  |  |  |  |  | 300 | 572 |
| T2A |  |  |  |  |  | 280 | 536 |
| T2B |  |  |  |  |  | 260 | 500 |
| T2C |  |  |  |  |  | 230 | 446 |
| T2D |  |  |  |  |  | 215 | 419 |
| T3 |  |  |  |  |  | 200 | 392 |
| T3A |  |  |  |  |  | 180 | 356 |
| T3B |  |  |  |  |  | 165 | 329 |
| T3C |  |  |  |  |  | 160 | 320 |
| T4 |  |  |  |  |  | 135 | 275 |
| T4A |  |  |  |  |  | 120 | 248 |
| T5 |  |  |  |  |  | 100 | 212 |
| T6 |  |  |  |  |  | 85 | 185 |

The user should make sure the temperature marking on approved equipment does not designate a temperature greater than the ignition temperature of the hazardous dust, fiber, gas or vapor of concern, even if the marked Class and Group meet the location requirements.